A First-Generation Integrated Continuous Bioprocessing Facility: Conceptual Design and Economic Analysis

Raymond Szuszkiewicz1^, Jeff Johnson2, Carrington Edmunds3, Ken Hamilton4, Brian Horowski1, Kelvin H. Lee5, Tom Piombino1, Juan Torres5, and John Erickson5

Affiliations:

1 IPS-Integrated Project Services; Blue Bell, PA, USA

2 Biotech Design LLC; Eagleville, PA, USA

3 AstraZeneca; Gaithersburg, MD, USA

4 Genentech; San Francisco, CA, USA

5 National Institute for Innovation in Manufacturing Biopharmaceuticals; Newark, DE, USA

^ Corresponding Author: Raymond Szuszkiewicz; IPS-Integrated Project Services, Blue Bell, PA, USA

- Contact Information: Raymond Szuszkiewicz 721 Arbor Way, Suite 100, Blue Bell, PA 19422; Email: rszuszkiewicz@ipsdb.com

Abstract

We present the design and economic analysis of a state-of-the-art commercial scale continuous biomanufacturing facility. Using current technology, equipment, quality and regulatory expectations, this design is described as a reference point against which new technology can be compared, and to illustrate the cost advantages of integrated continuous biomanufacturing. The facility can produce anywhere between 225kg to 3,600kg of mAbs per year, at a capital cost of approximately $200 million. ​This compares to a traditional 6x15kL SS facility, which can produce about 40% more (5,000kg/year) but has a capital cost at least 5 times higher (about $1 billion). A 20-year net present cost analysis showed that the continuous facility with bioreactor productivity of 5 g/L/day was favorable to the traditional 15kL six-pack at a titer of 5 g/L by hundreds of millions of dollars, even at production rates up to 6,400 kg/yr.

Keywords

Continuous biomanufacturing, facility design, flexible, single-use, economics, capital cost

Introduction

This work is part of an ambitious 10-year collaborative program to support invention, design, demonstration, and commercialization of biopharmaceutical manufacturing technology intended to transform the industry (Erickson et al.). One of the projects in that program is identifying and developing specific, shared objectives for collaboration on technologies, standards, and regulatory understanding that will enable the factories needed for the future. These objectives will lead to specific enabling projects which will be linked to specific attributes and business benefits, which will drive adoption. Business benefit can be measured in terms of economics, sustainability, quality, capital avoidance, speed, adherence to schedule, etc. The fact that specific information like facility designs, capital and operating costs is proprietary is a major challenge. To address this, we present a non-proprietary, state-of-the-art, high-level facility design and economic model than can serve as a common baseline to compare improvements. We call this the First Generation Factory and believe that everything is in place today to build it. A future paper will describe the next level of disruptive innovation that would be required to build a Second- Generation Factory. A goal of this work was to minimize capital and operating costs, so we chose to compare integrated/continuous bioprocessing (ICB) and single use systems with traditional batch and stainless steel facilities.

Process Overview

Starting with a published common platform for integrated and continuous bioprocessing (ICB) (Coffman et al.), a process was developed by a different NIIMBL project to produce a version of the NIST-mAb (NIST) and is shown in Figure 2. The process assumes a volumetric productivity of 5 g/L per day, a perfusion rate of 2.0 vessel volumes per day (VVD), and an overall yield of 64% in the downstream processing (DSP) steps.

The upstream process involves a traditional expansion, up to a 500-L single-use bioreactor (SUB), then to either a 4-kL SUB or two 2-kL SUBs running in parallel.  Only a few vendors currently offer a 4-kL SUB, so space was allocated in the layout to handle a two 2-kL SUB arrangement as well in an effort to keep the design vendor agnostic. Tangential flow filtration (TTF) or alternating tangential flow (ATF) can be used for perfusion.

The downstream purification process starts with  multi-column chromatography (MCC) with Protein A, continuous viral inactivation, flowthrough anion exchange chromatography (AEX), flowthrough multimodal chromatography, viral filtration, and single-pass TFF (SPTFF).  The drug substance is then filled into Cyrovaults ™ and taken to a blast freezer in the warehouse before being moved to a -40°C storage until it is shipped to a Drug Product Filling Facility.

Design Philosophy

A preliminary design was prepared for a flexible single use continuous mAb facility using currently existing technology, and that can meet today’s expectations for quality and regulatory practices. Workshops were held with eight NIIMBL member companies to refine the design philosophy and brainstorm ideas for improvement. It was decided that the facility would support low bioburden processing, with the potential to use rapid microbial detection and include at-line sampling and QC testing for real-time release. Waste break bag and process drains would be in a controlled non-classified (CNC) corridor. Cell Culture, Pre-viral Purification, Post-viral purification, and Media and Buffer Prep areas would be Grade D classified cleanrooms, with a separate CNC solution staging area (Logistics Center). The facility would follow Good Large-Scale Practice (GLSP), but no specific biosafety engineering control measures would be required. No compounds would require segregation or a biological containment boundary.

Facility Overview

The designed baseline facility, shown in Figure 3 and Figure 4, is 90,000 square feet, covering one and a half floors. An office mezzanine is located above the lab and entrance space for approximately 100 employees, which can be expanded or contracted as required based on the end user’s needs. Walkable ceilings are included above manufacturing, as well as an equipment platform to facilitate maintenance and house temperature control units, air handlers, and other support equipment.

The facility is designed for a flexible, end-to-end continuous biomanufacturing process, with 28-day batches and seven-day sublots that can produce between 225 and 3,600 kilograms of mAb drug substance, depending on the need. There is one 4,000 L bioreactor feeding the downstream train at all times. To accomplish this, two production bioreactors are included, so that while one is in production mode, the other is either being turned around, waiting or in growth phase. At a volumetric productivity of 5.0 g/L/d at a perfusion rate of 2.0 vessel volumes per day (VVD), the bioreactor output is 20 kg per day for a daily purified bulk production of approximately 12 kg. Sublots (up to 90 kg) are completed every seven days to optimize testing while minimizing production at risk. The process is primarily single-use except for the three stainless steel vessels supporting the buffer and media prep areas.

All utilities are in line with what you would find at a typical biopharmaceutical manufacturing facility: WFI generation, clean steam generation, and compressed air, with redundancy in all areas to ensure constant production.

Facility Layout

The use group diagram shown in Figure 5 illustrates the adjacencies of the major components of the facility: warehouse, utilities, labs, and manufacturing. The manufacturing area is further separated into support spaces for raw material sampling and staging, solution prep for buffer and media prep, and production. A logistics center spine divides the solution prep and production areas. The production line is only approximately 1/10 of the facility (~9,000 square feet). The only Grade C, ISO 8 space in the facility is Inoculum Prep. Walking through the layout, there is a unidirectional flow of materials from Inoculum Prep to a combined Grade D upstream (cell culture/pre-viral) area and then into the adjacent Grade D post-viral area.

Flows

Facility personnel maintain a bi-directional flow throughout the facility; however, the manufacturing process flow is unidirectional. Material flows for stock, buffer, media, and product are shown in Figure 6. The production path begins with shaker flasks inside the Inoculum Prep room, then moves through a pass box into the rocker bioreactors located in the Upstream / Pre-Viral Suite, then into 500-L SUBs, then into two 2-kL SUBs (or a single 4 kL SUB). The product continues to downstream chromatography steps and through the wall into the post-viral area for SPTFF, collection, and bulk filling into drug substance containers (Cryovaults ™ are used for example in the design). The Cryovaults ™ are palletized and brought to blast freezers, then moved to the –40°C cold storage area inside the warehouse.

Media is prepared as a 5x concentrate in a stainless steel prep tank or a single use mixer and is transferred to single use hold vessels (bags) in the CNC logistics center; the media is then transferred into the production rooms using tubing pass throughs to connect to the point of use.

For buffer prep, stock solutions are prepared in stainless steel prep tanks and stored in single use hold vessels (bags) in the Buffer Prep room before being fed into buffer stock blending (BSB) skids to formulate buffers for manufacturing.  Buffers can be concentrated up to 5x as required.  The buffer is then transferred to the single use hold vessels (bags) in the logistics center and, similar to media, is then transferred via tubing pass-throughs to their point of use in the production area.

Solutions Prep

Although many biomanufacturing facilities have combined media and buffer prep areas, the baseline facility design needed to be as non-controversial as possible to be presented as a good base case for comparison, so the decision was made to keep media and buffer prep separate. An additional small-scale single use mixer for media prep area was also included in the layout as shown in Figure 7.

Buffer prep is typically a labor-intensive operation to meet the demands of production. A buffer stock blending (BSB) skid, such as the one shown in Figure 8, can reduce the workload significantly as well as limit the amount of material that needs to be stored in the warehouse (Ram et al.). Single salt stock solutions are made as ~20x concentrates and stored in single use bags until they are fed into the BSB skid as needed. The blending skid formulates the buffers, which are stored in single use bags and drawn from the point of use. The facility uses solid charges to the buffer prep vessels with closed single-use powder bags and 5x concentrates for chromatography operations.  The overall buffer prep process is shown in Figure 9 and 10. The diafiltration buffers cannot be concentrated, so they remain at 1x. Sterilizing filters are replaced after every batch. Buffer top-offs allow the formulated storage bags to be used without changeout for the full 28-day duration of the batch.

Like buffer prep, 5x concentrated basal media is produced for 2 x 2-kL or 1 x 4-kL production SUBs and stored in jacketed bag holders, as shown in Figure 11. An adjacent cold room is available for storage at 2-8°C for smaller volume media. Sterilizing filters are replaced every two days with each media prep and top-off. The storage bags are used for the duration of the full 28-day batch. A CIP Skid is provided to clean the stainless steel prep tanks and transfer lines.

While only one BSB skid would be needed to meet the volume demands of the facility, the design plan includes two skids for redundancy. The same principle holds for the media and buffer prep vessels; a single vessel would be sufficient, but a second vessel is included in the design as a back-up.

Warehouse

The warehouse layout for this facility, as shown in Figure 11, is similar to most GMP facilities and houses slightly fewer than 700 pallets. While the footprint could potentially be reduced further with an automatic storage and retrieval system (ASRS), this approach does not become economically beneficial until the number of pallets are in the thousands.

The Cryovaults™ are designed to be loaded into a hold frame, with four frames being loaded onto a pallet. Each pallet is placed into a 2-8°C cold storage anteroom, then into a blast freezer, and then -40°C cold storage. A 2-8°C Cold Room acts as an anteroom for the –40°C Freezer Room and it holds the pre-packed chromatography columns as well.

Economic Analysis

As described above, the first-generation continuous biomanufacturing facility—explicitly designed to use existing technology—runs a 500-L perfusion bioreactor at a low titer up to a 4-kL perfusion bioreactor at a high titer to produce between 225 kg and 3600 kg of mAbs per year. Capital costs to build the facility were estimated to be slightly less than $200 million. As a benchmark, a traditional stainless steel 6 x 15-kL facility, which are built all over the world, at a titer of 5 g/L and a capacity of up to 5,000 kilograms a year, were estimated to have a capital cost exceeding $1 billion—five times the cost of the continuous facility.  The capital cost of a 6 x 2 kL single use fed batch facility is estimated to cost ~$200MM (+/-30%).  The capital costs and capacity of these facilities are summarized in Table I. The cost per capacity can be calculated by dividing the capital cost by the annual capacity.  A 6 x 15-kL stainless steel facility was estimated to be $208,000/kg/year, compared to $56,000/kg/year for the continuous facility—one-quarter the cost per kg capacity. Single-use 2 kL facility costs were estimated to be $156,000/kg/year and $313,000/kg/year for high and low titer outputs, respectively, as summarized in Figure 13.

The net present cost (NPC) was also estimated for each facility type and is shown in Figure 14. The NPC includes capital costs, facility operating costs, such as raw materials (e.g., resins and media) and single-use disposables, as well as labor requirements. Though NPC is often calculated over 10 years, this analysis was extended out to 20 years to account for the time needed to build a new factory and thus prevent overweighting of the NPC by the capital cost, particularly for stainless steel facilities. All costs over 20 years were discounted at a rate of 10 percent back to today’s dollars and the 20-year NPC was determined based on the target capacity of the facility in kilograms per year.

The 6 x 15-kL stainless steel facility (5 g/L titer) was estimated to cost $1.3 billion to build (based on industry benchmarks) and produce 300 kg per year for 20 years. At higher capacities, the 20-year NPC slowly increased, as capital costs make up the bulk of the cost of a stainless steel facility. Conversely, for single-use facilities, the capital costs were significantly lower, and the 20-year NPC was in the range of $200 to $250 million at a capacity of 300 kg per year. Due to the cost of disposables, however, the 20-year NPC for single-use facilities increases faster with increasing capacity due to the cost of the single use consumables.  A single-use facility with process intensification (perfusion) significantly increased the 20-year NPC due to the added cost of the perfusion media; at a production level over 3,000 kg per year, stainless steel would become a more cost-effective option. A single-use facility without perfusion and 10g/L titer (i.e., without the cost of media) would be more competitive against a stainless steel facility.

The 20-year NPC for the continuous facility was calculated at two scales, 2-kL perfusion and 4-kL perfusion. The NPCs at 300 kg per year capacity were slightly lower than for the single-use facilities, and increased at a lower slope than the fed batch facility due to the lower cost of single use consumable with a 28 day run time. Each curve showed an NPC jump when capacity was reached, due to the capital expenditure required for building the next facility. The NPC increase, however, is lower than the initial capital cost shown as the production rate is ramped up in each facility by 500 kg/year, and therefore facilities are built in the future and the capital costs are discounted by this time delay.  Importantly, however, the 20-year NPC for the continuous facility calculated at either scale was approximately $700 million lower than the traditional stainless steel facility and $200 million lower than single-use facilities, an advantage that persisted out to a capacity of 6,400 kg per year. A $100 million NPC advantage would be considered economically significant; the $200 to $700 million NPC advantage offered by the continuous facility was remarkable.

Several specific facility design factors directly contribute to the estimated $200 million capital cost, cost per capacity, and 20-year NPC for the first-generation continuous biomanufacturing facility compared to stainless steel and single-use facilities. The integrated continuous process helps shrink the facility footprint, as does the use of media concentrates. The inclusion of buffer stock blending skids to produce 5x concentrated buffers and dilute at the point of use significantly reduces labor costs and materials storage. Multicolumn chromatography utilizes 30% less buffer, and buffer and media top-offs also reduce the size and number of hold vessels needed. Single-use closed processing makes it possible to keep pre-viral and post-viral areas to Grade D, reducing the need for air locks and gowning, which lowers operating costs.

Conclusions

Integrated continuous biomanufacturing not only has more favorable economics compared to fed batch processes but is more flexible with a shorter construction schedule. Importantly, the first-generation baseline facility design presented here can be built using today’s technology, with no regulatory obstacles. We hope that the publication of this first-generation design will stimulate benchmarking and discussion by the industry which can lead to second and third generation facilities. Sharing knowledge is critical for growth and innovation in the biomanufacturing sector and to design the best facility possible.

Acknowledgements

This work was performed under a Project Award Agreement from the National Institute for Innovation in Manufacturing Biopharmaceuticals (NIIMBL) and financial assistance award 70NANB17H002 and 70NANB21H086 from the U.S. Department of Commerce, National Institute of Standards and Technology.

Conflict of Interest Declaration

The author(s) declare that they have no conflict of interests.

Table I – Facility Cost Comparison

| Facility | Productivity | Capacity | Capital Cost |
| --- | --- | --- | --- |
| 6 x 15kL SS | 5 g/L in 2 wks | 4800 kg/yr | >$1B |
| 6 x 2kL SU | 5 g/L in 2 wks | 640 kg/yr | ~$200MM |
| 6 x 2kL SU | 10 g/L in 2 wks | 1280 kg/yr | ~$200MM |
| 1 x 4kL Continuous | 5 g/L/d | 3600 kg/yr | ~$200MM |

Figure Captions

Figure 1 – Interior Rendering of Manufacturing Suite

Figure 2 – Process Block Flow Diagram

Figure 3 – Manufacturing Floor Plan

Figure 4 – Overall Floor Plan – First Floor

Figure 5 – Use Group Diagram

Figure 6 – Material Flow Diagram

Figure 7 – Solution Prep Floor Plan

Figure 8 – NIIMBL Biophorum Buffer Stock Blending Skid located at NIIMBL Headquarters at the University of Delaware

Figure 9 – Buffer Prep Block Flow Diagram

Figure 10 – Buffer Prep – Process Flow Diagram

Figure 11 – Media Prep – Process Flow Diagram

Figure 12 – Warehouse Floor Plan

Figure 13 – Capital Costs Divided by Annual Capacity Comparison

Figure 14 – Net Present Cost (20 years) Comparison

Coffman, J. et al. "The Design Basis for the Integrated and Continuous Biomanufacturing Framework." Biotechnol Bioeng, vol. 118, no. 9, 2021, pp. 3323-33, doi:10.1002/bit.27697.

Erickson, J et al. "End-to-End Collaboration to Transform Biopharmaceutical Development and Manufacturing." Biotechnology and Bioengineering, vol. 118, no. 9, 2021, pp. 3302-12, doi:10.1002/bit.27688.

NIST. "Nist Monoclonal Antibody Reference Material 8671." https://www.nist.gov/programs-projects/nist-monoclonal-antibody-reference-material-8671. Accessed 2/4/2025 2025.

Ram, N. et al. "Evaluation of the Design, Development, and Performance of a Mass-Flow Based, Open-Source Buffer Manufacturing System." PDA J Pharm Sci Technol, vol. 77, no. 2, 2023, pp. 79-98, doi:10.5731/pdajpst.2021.012660.