A First-Generation Integrated Continuous Bioprocessing Facility: Conceptual Design and Economic Analysis

Raymond Szuszkiewicz1^, Jeff Johnson2, Carrington Edmunds3, Ken Hamilton4, Brian Horowski1, Kelvin H. Lee5, Behnam Partopour6, Tom Piombino1, Juan Torres5, and John Erickson5

Affiliations:

1 IPS-Integrated Project Services; Blue Bell, PA, USA

2 Biotech Design LLC; Eagleville, PA, USA

3 AstraZeneca; Gaithersburg, MD, USA

4 Genentech; San Francisco, CA, USA

5 National Institute for Innovation in Manufacturing Biopharmaceuticals; Newark, DE, USA

6 Sartorius Corporate Research, Marlborough, MA, USA

^ Corresponding Author: Raymond Szuszkiewicz; IPS-Integrated Project Services, Blue Bell, PA, USA

- Contact Information: Raymond Szuszkiewicz 721 Arbor Way, Suite 100, Blue Bell, PA 19422; Email: rszuszkiewicz@ipsdb.com

Abstract

We present the design and economic analysis of a state-of-the-art commercial scale continuous biomanufacturing facility. Using current technology, equipment, quality and regulatory expectations, this design is described as a reference point against which new technology can be compared, and to illustrate the cost advantages of integrated continuous biomanufacturing. The facility can produce anywhere between 225kg to 3,600kg of mAbs per year, at a capital cost of approximately $210 million. ​This compares to a traditional 6x15kL SS facility, which can produce about 40% more but has a capital cost at least 6 times higher (about $1.3 billion). A 20-year net present cost analysis showed that the continuous facility with bioreactor volumetric productivity of 5 g/L bioreactor/day was favorable to the traditional 15kL six-pack at a titer of 10 g/L by hundreds of millions of dollars, even at production rates up to 10,000 kg/yr.

Keywords

Continuous biomanufacturing, facility design, flexible, single-use, economics, capital cost

Introduction

This work is part of an ambitious 10-year collaborative program to support invention, design, demonstration, and commercialization of biopharmaceutical manufacturing technology intended to transform the industry (Erickson et al.). One of the projects in that program is identifying and developing specific, shared objectives for collaboration on technologies, standards, and regulatory understanding that will enable the factories needed for the future. These objectives will lead to specific enabling projects which will be linked to specific attributes and business benefits, which will drive adoption. Business benefit can be measured in terms of economics, sustainability, quality, capital avoidance, speed, adherence to schedule, etc. The fact that specific information like facility designs, capital and operating costs is proprietary is a major challenge. To address this, we present a non-proprietary, state-of-the-art, high-level facility design and economic model than can serve as a common baseline to compare improvements. We call this the First Generation Factory and believe that everything is in place today to build it. A future paper will describe the next level of disruptive innovation that would be required to build a Second Generation Factory. A goal of this work was to minimize capital and operating costs, so we chose to compare integrated/continuous bioprocessing (ICB) and single use systems with traditional batch and stainless steel facilities. Figure 1 is a rendering of the process area of the facility.

Process Overview

Starting with a published common platform for integrated and continuous bioprocessing (ICB) (Coffman et al.), a process was developed by a different NIIMBL project to produce a version of the NIST-mAb (NIST) and is shown in Figure 2. The process assumes a volumetric productivity of 5 g/L bioreactor per day, a perfusion rate of 2.0 vessel volumes per day (VVD), and an overall yield of 64% in the downstream processing (DSP) steps,resulting in a maximum capacity of 3600 kg of mAb per year.

The upstream process involves a traditional expansion, up to a 500-L single-use bioreactor (SUB), then to either a 4-kL SUB or two 2-kL SUBs running in parallel.  Only a few vendors currently offer a 4-kL SUB, so space was allocated in the layout to handle a two 2-kL SUB arrangement as well in an effort to keep the design vendor agnostic. Tangential flow filtration (TTF) or alternating tangential flow (ATF) can be used for perfusion.

The downstream purification process starts with multi-column chromatography (MCC) with Protein A, continuous viral inactivation, flowthrough anion exchange chromatography (AEX), flowthrough multimodal chromatography, viral filtration, and single-pass TFF (SPTFF).  The drug substance is then filled into Cryovaults ™ and taken to a blast freezer in the warehouse before being moved to a -40°C storage area until it is shipped to a Drug Product Filling Facility.

Design Philosophy

A preliminary design was prepared for a flexible single use continuous mAb facility using currently existing technology, and that can meet today’s expectations for quality and regulatory practices. Workshops were held with eight NIIMBL member companies to refine the design philosophy and brainstorm ideas for improvement. It was decided that the facility would support low bioburden processing, with the potential to use rapid microbial detection and include at-line sampling and QC testing for real-time release. Waste break bag and process drains would be in a controlled non-classified (CNC) corridor. Cell Culture, Pre-viral Purification, Post-viral purification, and Media and Buffer Prep areas would be Grade D classified cleanrooms, with a separate CNC solution staging area (Logistics Center). The facility would follow Good Large-Scale Practice (GLSP), but no specific biosafety engineering control measures would be required. No compounds would require segregation or a biological containment boundary.

Facility Overview

The designed baseline facility, shown in Figure 3 and Figure 4, is 90,000 square feet, covering one and a half floors. An office mezzanine is located above the lab and entrance space for approximately 100 employees, which can be expanded or contracted as required based on the end user’s needs. Walkable ceilings are included above manufacturing, as well as an equipment platform to facilitate maintenance and house temperature control units, air handlers, and other support equipment.

The facility is designed for a flexible, end-to-end continuous biomanufacturing process, with 28-day batches that can produce between 225 and 3,600 kilograms of mAb drug substance per year, depending on the need. There is one 4,000 L bioreactor feeding the downstream train at all times. To accomplish this, two production bioreactors are included, so that while one is in production mode, the other is either being turned around, waiting or in growth phase. At a volumetric productivity of 5.0 g/L/d at a perfusion rate of 2.0 vessel volumes per day (VVD), the bioreactor output is 20 kg per day for a daily purified bulk production of approximately 12 kg. Sublots (up to 90 kg) are completed every seven days to optimize testing while minimizing production at risk. The process is primarily single-use except for the three stainless steel vessels supporting the buffer and media prep areas.

All utilities are in line with what you would find at a typical biopharmaceutical manufacturing facility: WFI generation, clean steam generation, and compressed air, with redundancy in all areas to ensure constant production.

Facility Layout

The use group diagram shown in Figure 5 illustrates the adjacencies of the major components of the facility: warehouse, utilities, labs, and manufacturing. The manufacturing area is further separated into support spaces for raw material sampling and staging, solution prep for buffer and media prep, and production. A logistics center spine divides the solution prep and production areas. The production line is only approximately 1/10 of the facility (~9,000 square feet). The only Grade C, (ISO 8 in operation) space in the facility is Inoculum Prep. Walking through the layout, there is a unidirectional flow of materials from Inoculum Prep to a combined Grade D (ISO 8 at rest) upstream (cell culture/pre-viral) area and then into the adjacent Grade D post-viral area.

Flows

Facility personnel maintain a bi-directional flow throughout the facility; however, the manufacturing process flow is unidirectional. Material flows for stock, buffer, media, and product are shown in Figure 6. The production path begins with shaker flasks inside the Inoculum Prep room, then moves through a pass box into the rocker bioreactors located in the Upstream / Pre-Viral Suite, then into 500-L SUBs, then into two 2-kL SUBs (or a single 4 kL SUB). The product continues to downstream chromatography steps and through the wall into the post-viral area for SPTFF, collection, and bulk filling into drug substance containers. The containers are palletized and brought to blast freezers, then moved to the –40°C cold storage area inside the warehouse.

Base medium is prepared as a 5x concentrate in a stainless steel prep tank or a single use mixer and is transferred to single use hold vessels (bags) in the CNC logistics center; the medium is then transferred into the production rooms using tubing pass throughs to connect to the point of use. The design can accommodate up to two additional feeds to the bioreactor.

For buffer prep, single component stock solutions are prepared in stainless steel prep tanks and stored in single use hold vessels (bags) in the Buffer Prep room before being fed into buffer stock blending (BSB) skids to formulate buffers for manufacturing.  Buffers can be formulated in the buffer skid at up to 5x concentration.  The buffer is then transferred to the single use hold vessels (bags) in the logistics center and, similar to media, is then transferred via tubing pass-throughs to their point of use in the production area.

Solutions Prep

Although many biomanufacturing facilities have combined media and buffer prep areas, the baseline facility design needed to be as non-controversial as possible to be presented as a good base case for comparison, so the decision was made to keep media and buffer prep separate. An additional small-scale single use mixer for media prep area was also included in the layout as shown in Figure 7.

Buffer prep is typically a labor-intensive operation to meet the demands of production. A buffer stock blending (BSB) skid, such as the NIIMBL-BioPhorum open source BSB skid shown in Figure 8, can reduce the workload significantly as well as limit the amount of material that needs to be stored in the warehouse (Ram et al.). Single salt stock solutions are made as ~20x concentrates and stored in single use bags until they are fed into the BSB skid as needed. The blending skid formulates the buffers, which are stored in single use bags and drawn from the point of use. The facility uses solid charges to the buffer prep vessels with closed single-use powder bags and 5x concentrates for chromatography operations.  The overall buffer prep process is shown in Figure 9 and 10. The diafiltration buffers cannot be concentrated, so they remain at 1x. Sterilizing filters are replaced after every batch. Buffer top-offs allow the formulated storage bags to be used without changeout for the full 28-day duration of the batch.

Like buffer prep, 5x concentrated basal medium is assumed to be produced for 2 x 2-kL or 1 x 4-kL production SUBs and stored in jacketed bag holders, as shown in Figure 11. An adjacent cold room is available for storage at 2-8°C for smaller volume media. Sterilizing filters are replaced every two days with each media prep and top-off. The storage bags are used for the duration of the full 28-day batch. A CIP Skid is provided to clean the stainless steel prep tanks and transfer lines.

While only one BSB skid would be needed to meet the volume demands of the facility, the design plan includes two skids for redundancy. The same principle holds for the media and buffer prep vessels; a single vessel would be sufficient, but a second vessel is included in the design as a back-up.

Warehouse

The warehouse layout for this facility, as shown in Figure 11, is similar to most GMP facilities.It houses slightly fewer than 700 pallets. While the footprint could potentially be reduced further with an automatic storage and retrieval system (ASRS), this approach does not become economically beneficial until the number of pallets is in the thousands.

The Cryovaults™ are designed to be loaded into a hold frame, with four frames being loaded onto a pallet. Each pallet is placed into a 2-8°C cold storage anteroom, then into a blast freezer, and then -40°C cold storage. A 2-8°C Cold Room acts as an anteroom for the –40°C Freezer Room and it holds the pre-packed chromatography columns as well.

Economic Analysis

The first-generation continuous facility described above was estimated to cost about $210 million and take 3 years to build and qualify. As a benchmark, traditional stainless steel 6 x 15-kL facilities, at a titer of 10 g/L and capacity of up to 9,600 kilograms a year, were estimated to have a capital cost of about $1.3 billion—six times the cost of the continuous facility, and take 4 years to build and qualify through IQ/OQ completion.  A 6 x 4 kL single use fed batch facility with titer of 10 g/L is estimated to cost about $260MM and take 3 years to build and qualify. The capital cost and capacity of these facilities are summarized in Table I. COST ESTIMATES WERE DETERMINED BY … The capital cost per kg of capacity can be calculated by dividing the capital cost by the annual capacity and is summarized in Figure 13. Note that both single use facilities are favorable to the stainless facility in this measure as would be expected, but our continuous design is much more favorable than single use fed batch.

The operating costs were calculated using BioSolve process modeling software. The consumable and raw material costs were estimated using internal data and are aligned with a recently published paper by Neves et al. (2024). To preserve the confidentiality of itemized list prices, we report only aggregate consumables and raw-material costs on a per-gram basis. Direct labor hours were first estimated for each unit-operation recipe step—processing, cleaning, and preparation—using the step-specific personnel count and duration. These hours were then translated into required staffing coverage by applying the relevant shift patterns and durations (e.g., 24-h operation for upstream). Based on the operational shift pattern and average daily demand, we generated team rosters that met total effort without breaching constraints such as maximum weekly hours per person. Requirements were subsequently adjusted for utilization, annual operative availability, and overhead factors. Finally, full-time-equivalent (FTE) needs were calculated for each process area and other labor categories (e.g., supervisors) as fixed ratios to the direct operator FTEs. Overhead costs comprise: (i) maintenance and insurance, applied as a fixed percentage of annual costs; (ii) utilities, estimated from facility energy and water demand; and (iii) waste management, calculated from treatment costs for total aqueous and plastic wastes. These costs are summarized in Table 2.

The net present cost (NPC) was also estimated for each facility type. The NPC discounts cash flows to the present, includes capital, operating costs such as raw materials (e.g., resins and media) and single-use disposables, as well as labor and overhead. This analysis covered 20 years to account for the time needed to build and depreciate a factory. The discount rate was 10 percent.

The analysis assumes the facility is being built in years 1 through 4. For the facilities that only take 3 years to build, construction and capital spend don’t start until year 2. In year 5, we assume the plant starts production and that demand and production increase linearly for 10 years and then peak demand is reached. After that, production stays at peak. In cases where demand exceeds the capacity of the existing facility, we assume that additional facilities are built just in time to keep up with demand. We also assumed that a continuous improvement program increased productivity by 3% year on year.

Figure 14 shows the NPC on the y-axis and the peak demand on the x-axis for the three scenarios shown in Table 1. The lines increase linearly as peak demand increases, except when increasing the peak demand requires an additional facility to be built. At that point, the line jumps up to include the NPC of the capital of the additional facility required. Recall that we assume a 3% YOY productivity increase, so the lines jump up at higher demand than the initial plant capacities listed in Table 1. When peak demand is low, only one of any of the facility types are needed, so the SU facilities, which have much lower capital cost come out ahead. The slopes of the SU lines are higher than the slope of the SS line because of the impact of the single-use consumables needed for each batch. The slope for the SU continuous facility is lower than that for the SU fed-batch facility because most of the SU components are changed out a lot more often in the batch facility than the continuous facility.

The continuous facility has a lower NPC than both fed batch facilities over all peak demand scenarios. The NPC of the continuous SU facility is less than the fed-bx SS facility by $1 billion at the lowest peak demand and the difference gradually diminishes until the SS facility reaches full capacity. At higher peak demand, when a second SS facility is required, however, the difference goes back to up to about $800MM. The SU continuous facility is always less expensive than the SU fed batch, and the difference gets bigger the higher the peak demand. The conventional wisdom is that large stainless steel facilities are better for high volume products while smaller single use facilities are better for small volume products. Our analysis shows that this is true when comparing SU and SS when both use fed-batch, but our first-generation single use continuous facility out-performs the large stainless facility even at high volumes. This is especially true if demand is uncertain and there is a chance that one big stainless steel facility isn’t big enough, but a second facility would run at low utilization.

Several specific facility design factors directly contribute to the estimated capital cost, cost per capacity, and 20-year NPC for the first-generation continuous biomanufacturing facility compared to stainless steel and single-use facilities. The integrated continuous process helps shrink the facility footprint, as does the use of media concentrates. The inclusion of buffer stock blending skids to produce 5x concentrated buffers and dilute at the point of use significantly reduces labor costs and materials storage. Multicolumn chromatography utilizes 30% less buffer, and buffer and media top-offs also reduce the size and number of hold vessels needed. Single-use closed processing makes it possible to keep pre-viral and post-viral areas to Grade D, reducing the need for air locks and gowning, which lowers operating costs.

Conclusions

Integrated continuous biomanufacturing not only has more favorable economics compared to fed batch processes but is more flexible. Importantly, the first-generation baseline facility design presented here can be built using today’s technology, with no regulatory obstacles. We hope that the publication of this first-generation design will stimulate benchmarking and discussion by the industry which can lead to second and third generation facilities. Sharing knowledge is critical for growth and innovation in the biomanufacturing sector and to design the best facility possible.

Acknowledgements

This work was performed under a Project Award Agreement from the National Institute for Innovation in Manufacturing Biopharmaceuticals (NIIMBL) and financial assistance award 70NANB17H002, 70NANB21H085, and 70NANB21H086 from the U.S. Department of Commerce, National Institute of Standards and Technology.

Conflict of Interest Declaration

The author(s) declare that they have no conflict of interests.

Table I – Facility Cost Comparison

| Facility | Cell Culture Productivity | Capacity | Approximate Capital Cost |
| --- | --- | --- | --- |
| 6 x 15kL SS | 10 g/L in 2 wks | 9600 kg/yr | $1.3B |
| 6 x 4kL SU | 10 g/L in 2 wks | 2800 kg/yr | $260MM |
| 1 x 4kL Continuous | 5 g/L/d | 3600 kg/yr | $210MM |

Table 2 – Operating Cost Comparison

| Facility | Raw Materials and Consumables | Annual Labor | Overhead |
| --- | --- | --- | --- |
| 6 x 15kL SS | $22 g | $60 MM/yr | $50M |
| 6 x 4kL SU | $30 g | $57 MM/yr | $13M |
| 1 x 4kL Continuous | $27 g | $39 MM/yr | $13M |

Figure Captions

Figure 1 – Interior Rendering of Manufacturing Suite

Figure 2 – Process Block Flow Diagram

Figure 3 – Manufacturing Floor Plan

Figure 4 – Overall Floor Plan – First Floor

Figure 5 – Use Group Diagram

Figure 6 – Material Flow Diagram

Figure 7 – Solution Prep Floor Plan

Figure 8 – NIIMBL Biophorum Buffer Stock Blending Skid located at NIIMBL Headquarters at the University of Delaware

Figure 9 – Buffer Prep Block Flow Diagram

Figure 10 – Buffer Prep – Process Flow Diagram

Figure 11 – Media Prep – Process Flow Diagram

Figure 12 – Warehouse Floor Plan

Figure 13 – Capital Costs Divided by Annual Capacity Comparison

Figure 14 – Net Present Cost (20 years) Comparison

Coffman, J. et al. "The Design Basis for the Integrated and Continuous Biomanufacturing Framework." Biotechnol Bioeng, vol. 118, no. 9, 2021, pp. 3323-33, doi:10.1002/bit.27697.

Erickson, J et al. "End-to-End Collaboration to Transform Biopharmaceutical Development and Manufacturing." Biotechnology and Bioengineering, vol. 118, no. 9, 2021, pp. 3302-12, doi:10.1002/bit.27688.

NIST. "Nist Monoclonal Antibody Reference Material 8671." https://www.nist.gov/programs-projects/nist-monoclonal-antibody-reference-material-8671. Accessed 2/4/2025 2025.

Ram, N. et al. "Evaluation of the Design, Development, and Performance of a Mass-Flow Based, Open-Source Buffer Manufacturing System." PDA J Pharm Sci Technol, vol. 77, no. 2, 2023, pp. 79-98, doi:10.5731/pdajpst.2021.012660.

Neves, C. et al. “Evaluating end‐to‐end continuous antibody manufacture with column‐free capture alternatives from economic, environmental, and robustness perspectives” Biotechnology Progress, 40(4), 2024,  https://doi.org/10.1002/btpr.3427